SECTION 23 34 33

AIR CURTAINS

Berner Commercial High Performance 10 Series (CHD10) air curtains (a.k.a. air doors) are designed to be competitively priced for use at customer entry and service entry doors.  They are suitable for opening heights up to 10 ft (304.8 cm) for environmental separation and up to 8 ft (243.8 cm) for insect control.

### Air curtains provide environmental separation at openings by reducing the infiltration of unconditioned air, fumes, dust, and humidity.  At exterior openings, they can resist winds up to 10 MPH (16 KPH) and are generally mounted inside the building. During cold seasons warm air that has risen towards ceiling is recirculated; they can also be used at interior openings such as doors to coolers or clean rooms.  Optimum protection is provided when units are mounted flush to the wall and as close to top of door opening as possible.   To ensure peak performance keep air stream free of obstructions.  Air curtains may not be fully effective where negative air pressure exists on one side of door; contact Berner for additional information.

Series CHD10 model air curtains have 1/2 HP motors.  They can be wall mounted or suspended from the ceiling.  Electric heated units shall be installed indoors only and require – a minimum clearance of at least 6 ft (182.9 cm) between the bottom of the unit and the floor, a minimum of 8 in (20.3 cm) between the top and ceiling and 1 in (2.5 cm) between the sides and any combustible material.

Edit guide specification to include only information specific to your project.  Delete or add text, select appropriate bracketed phrases, and fill in blanks as required. Go to Berner catalog or website (www.Berner.com) to select specific models and sizes that are required for project and to obtain data necessary to edit this document.

Coordinate specification with information shown on project drawings and schedules.  In general, drawings indicate locations of air curtains and switches and special mounting requirements, while sizes and capacities of air curtains and utilities should be described in specifications or schedules.  Cross check mechanical and architectural drawings.

This guide specification is available in word processing format at www.berner.com.  Turn on “Hidden Text” function in your word processor to display “Specifier Notes.”

For additional information or name of Berner representative in your area, call Berner International Corporation at 800-245-4455 in U.S. or 800-242-4455 in Canada, or visit www.Berner.com. A selection guide is available at www.Berner.com to suggest models appropriate for typical applications.

GENERAL

CONDITIONS AND REQUIREMENTS

The General Conditions, Supplementary Conditions, and Division 01 – General Requirements apply.

SECTION INCLUDES

Specifier Note:  Delete items below that are not included in this section. Retain only those options in the first paragraph below that are required for a specific project.

Air curtains[, electric heated].

[Insert item description.]

RELATED REQUIREMENTS

Specifier Note:  In this article, specify work specified in other sections that is related to work of this section.

Section 04 22 00 - Concrete Unit Masonry:  Blocking or reinforcing in wall as required for attachment of air curtain.

Section 05 40 00 - Cold-Formed Metal Framing:  Reinforcing in wall as required for attachment of air curtain.

Section 06 10 00 - Rough Carpentry:  Blocking in wall as required for attachment of air curtain.

Specifier Note: If switches for air curtains are mounted on door frames, retain either Section 08 11 00 or 08 41 00 below to facilitate coordination.

Section 08 11 00 - Metal Doors and Frames:  Coordinate installation of switches.

Section 08 41 00 - Entrances and Storefronts:  Coordinate installation of switches.

Specifier Note:  Retain the following paragraph if door openers or automatic door opening assemblies are used.  Air door must be positioned so air stream is not obstructed when deflected 20 degrees to either side of centerline.  If air stream strikes any obstruction (top edge of the doorway, door opening device, etc.) effectiveness of unit will be reduced.

Section 08 71 00 - Door Hardware:  Coordinate with installation of hardware.

Specifier Note:  Retain any of the three following paragraphs if air curtains are mounted above ceiling.  Delete if no units installed above ceiling.

Section 09 22 16 - Non-Structural Metal Framing:  Framing and blocking above ceiling as required for installation of air curtain.

Section 09 29 00 - Gypsum Board:  Ceiling finish abutting air curtain.

Section 09 51 13 - Acoustical Panel Ceilings:  Ceiling finish abutting air curtain.

Specifier Note:  Retain the first paragraph below if air curtain cabinets are to be field painted.  Protect electrical contacts and moveable parts from paint.

Section 09 91 00 - Painting:  Field applied finishes.

Division 26 - Electrical:  Connection of electrical service and controls.

Specifier Note:  The following paragraph is a sample that may be used in this article.  Add to or delete from the following as appropriate for the specific project.

Section [xxxxx] – [Section Title]:  [Include brief description of work specified in another section that is related to the work of this section.]

REFERENCE STANDARDS

Air Movement & Control Association International, Inc. (AMCA):

AMCA 211 - Certified Ratings Program - Product Rating Manual for Fan Air Performance.

AMCA 220 - Laboratory Methods of Testing Air Curtains for Aerodynamic Performance Ratings.

AMCA 222 - Application Manual for Air Curtain Units.

National Electrical Manufacturers Association (NEMA):

NEMA 250 - Enclosures for Electrical Equipment (1000 Volts Maximum).

Underwriters Laboratories (UL):

UL 507 - Electric Fans.

UL 2021 - Fixed and Location-Dedicated Electric Room Heaters.

SUBMITTALS

Specifier Note:  In this article, specify various types of data to be furnished by the contractor before, during, or after construction. Topics included in this article are:  product data, shop drawings, samples, design data, test reports, certificates, manufacturers’ instructions, manufacturers’ field reports, qualification statements, and closeout submittals.

Submit under provisions of Section [01 33 00] [______].

Product Data:  Submit for [____________] including:

[_____________________.]

Rated capacities.

Operating characteristics.

Accessories.

Options.

Shop Drawings:  For air curtain components not adequately described by product data.  Show configuration of non-standard units.  Include plans, elevations, sections, details, and attachments to other work.

Indicate dimensions, weights, loads, clearances required, location and size of field connections.

Provide wiring diagrams for power, signal, and control wiring.

Operation and Maintenance Data:  For air curtains to include in maintenance manuals.

Warranties:  Sample of special warranties.

QUALITY ASSURANCE

Specifier Note:  In this article, describe qualifications, regulatory requirements, certifications, field samples, mock-ups, and pre-installation meetings.

Manufacturers:  Firms regularly engaged in manufacture of air curtains of the types and sizes required, whose products have been in satisfactory use in similar service for not less than 10 years.  Provide air curtains produced by a manufacturer listed in this section.

Source Limitations:  Obtain each type of air curtain through one (1) source from a single manufacturer.

Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Comply with AMCA 211 for airflow rate, average outlet velocity, outlet velocity uniformity, velocity projection and power rating.

Certification:

Test units in accordance with AMCA 220.  Provide units licensed to bear the AMCA Certified Ratings Seal.

Units shall comply with applicable United States and Canadian Standards. Provide units authorized to bear the UL and cUL marks.

DELIVERY, STORAGE AND HANDLING

Deliver air curtains in factory labeled packages.

Store and handle in strict compliance with manufacturer’s written instructions and recommendations.

Protect from damage due to weather, excessive temperature, and construction operations.

WARRANTY

Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of air curtains that fail in materials or workmanship within specified warranty period.

Specifier Note:  Retain either of the following two subparagraphs to agree with type of unit selected for a project and delete the other. Retain both subparagraphs if project has both types of units.

Five-year limited warranty for unheated units.

Two-year limited warranty for heated units.

PRODUCTS

MANUFACTURERS

Basis-of-Design Manufacturer:  The design for air curtains is based on products manufactured by Berner International Corporation, 111 Progress Avenue, New Castle; PA, Telephone: 724-658-3551; Toll-Free Telephones: 800-245-4455 (U.S.), 800-242-4455 (Canada); Fax: 724-652-0682; email: airdoors@berner.com; Website: www.berner.com.

Specifier Note:  Retain one of the following two paragraphs and delete the other.

Substitutions are not permitted.

Substitutions will be considered under provisions of Section 01 60 00.

AIR CURTAINS

Specifier Note: Retain model types in the following paragraph as required for specific project. Delete those that are required.

Acceptable Products:  Berner Commercial High Performance 10 Model [CHD10 Ambient] [CHD10 Electric Heated].

Construction:  Provide factory-assembled units of sufficient structural strength to be supported from ends without intermediate support.  Ship units completely assembled.

Cabinet:

Specifier Note: Retain one of the options in the following subparagraph.  Standard cabinet construction is riveted mill aluminum with aluminum white on white polyester painted or black powder coated aluminum cover; optional cover available in stainless steel or custom color powder coated aluminum.

Material and Finish:  Aluminum base frame with stainless steel riveted construction and [white on white polyester painted aluminum] [black powder coated aluminum] [stainless steel] [[insert color selection] powder coated aluminum] cover.  [Tamper-resistant construction; parts cannot be disassembled without special tool provided by manufacturer.]

Dimensions:  Not to exceed 14.25 in (36.2 cm) high by 15 in (38.1 cm) deep.

Specifier Note:  Retain only the mounting method required for a specific project in the following subparagraph and delete the others.

Mounting:  Provide for [wall] [suspended] mounting.

Service Access: Removable combination screen and bottom access panel.

Motors:  1/2-HP, 1680 RPM, single phase, 3-speed, ODP, direct drive, resilient mounted, continuous duty, with internal thermal-overload protection and permanently lubricated sealed ball bearings.

Fans:  Balanced forward curved type, double inlet, mounted in matched fan housings with aerodynamically formed air inlet venturis.  Manufacture wheels and housings from galvanized steel.

Discharge Nozzles:

Provide uniform velocity across width of air curtain.

Aperture:  3.5 inch (9 cm) slot by width of air curtain.

Vanes:  1.5 in (3.8 cm) minimum height; constructed of airfoil-shaped aluminum extrusions; adjustable plus or minus 20 degrees to deflect airflow.

Specifier Note:  Retain the following paragraph for all unheated and heated units installed above the ceiling.  Extensions are either provided constructed from 21 in (53.3 cm) high aluminized steel suitable for field cutting to length or fixed 6 in (15.2 cm) high clear anodized aluminum.  Standard air directional vanes are aluminum, while white aluminum multi-blade air discharge grilles are optional.

Nozzle Extension:  [Unpainted aluminized steel] [Clear anodized aluminum] with airfoil shaped [1.5 in (3.8 cm) aluminum discharge vanes] [0.875 in (2.2 cm) white aluminum multi-blade air discharge grille].

Inlet:

Location: Front.

Screen:  Perforated pattern constructed of the same material and finish used for the cover.

Specifier Note:  Retain the following paragraph if optional filters are required for a specific project.

Air Inlet Filter:  Flat-faced fire rated re-cleanable aluminum with integral filter clips.

Specifier Note:  Retain the following article if heated units are required for a specific project.

HEATING ELEMENTS

Electric Heating Coil:  UL-approved, factory-mounted, factory-wired, thermally-protected, galvanized steel frame.

Venturi mounted helical coil with point suspended elements, [single] [three] phase circuit.

Thermal Cutout: Locks out electric heater when prolonged abnormal over-temperature conditions exist.

CONTROLS

Specifier Note: Select the location of the control switches. Unit mounted switches are standard on all units.

Switching:

Specifier Note: Retain the following subparagraph for use with unheated models.

Manual Switch:  [Factory installed “Fan On-Off” and “High-Med-Low” switches] [Remote mount 5 position rotary cam Fan Off-High-Med-Low switch].

Specifier Note: Retain the following subparagraph for use with electric heated models.

Manual Switch:  [Factory installed “Fan-Off-Fan & Heat” and “High-Med-Low” switches] [Remove mount 7 position rotary cam “Low-Med-High-Off-Hi & Heat-Med & Heat-Low & Heat” switch].

Specifier Note:  Retain one of the following three paragraphs and delete the other two.  In the first paragraph the air curtain turns on when door is opened and shuts off when door is closed.  This package can be used on both heated and unheated units.

Basic Control Package:  Air curtain turns on when door is opened and shuts off when door is closed.

Specifier Note:  Retain either Line Voltage Control or 24V Control the following subparagraph and delete the other one.  Retain door switch type and delete the others

Line Voltage Control:  [NEMA [1] [4] plunger] [NEMA 1 roller] style door switch.

24 Volt Control:  [NEMA [1] [4] plunger] [NEMA 1 roller] [Magnetic reed] style door switch and factory-installed transformer.

Specifier Note:  In the following paragraph the air curtain turns on when door is opened and shuts off after the door is closed and the set delay time expires.  This package can be used on both heated and unheated units.

Deluxe Control Package:  Air curtain turns on when door is opened and shuts off when door is closed, unit remains on until set delay time expires.

Specifier Note:  Retain either Line Voltage Control or 24V Control the following subparagraph and delete the other one.  Where applicable retain door switch type for a specified project.

Line Voltage Control:  [NEMA [1] [4] plunger] [NEMA 1 roller] style door switch and factory-installed time delay.

24 Volt Control:  [NEMA [1] [4] plunger] [NEMA 1 roller] [Magnetic reed] style door switch and factory-installed time delay.

Specifier Note:  Retain the following paragraph only if three speed electric heated units are required for a specific project.

Comfort Plus 24 Volt Control Package:  Provides supplemental heat when door is closed and allows the air curtain to run at the speed selected to protect the opening when the door is opened.  The air curtain shuts off after the door is closed and the set delay time expires. When the door is closed and the temperature drops below the set point the air curtain runs at low speed providing supplemental heat until the thermostat is satisfied.

Provide package complete with [magnetic reed] [NEMA [1] [4] plunger] [NEMA 1 roller arm] style door switch, factory-installed transformer, time delay and thermostat.

Specifier Note:  Retain the following paragraph when specifying electric heated units when thermostat is not included in a control package.

Thermostat:  Prevents operation of heater when inside air temperature exceeds desired temperature.

Specifier Note:  Retain the following paragraph if a disconnect switch is required to simplify power shut-off when servicing air curtain.

Disconnect Switch:  Provide lockable remote mounted non-fused toggle disconnects based on number of power supplies required.

Specifier Note:  Retain the following paragraph and insert text describing coordinating operational sequence of air curtain controls if required.

Sequencing:  [______________________________.]

MOUNTING ACCESSORIES

Specifier Note:  Show wall mounting plate on Drawings if required.

Provide wall mounting plate and other mounting accessories as required to permit installation and proper functioning of air curtain to meet project conditions of use.

Specifier Note:  Retain the applicable wall mounting plate from the list below and delete those not required for a project.  Standard Wall Plate material is aluminized steel with white powder coated finish.

Wall Mounting Plate: [aluminized steel with [white] [black] [insert color selection] powder coated finish] [stainless steel].

EXECUTION

EXAMINATION

Verify that door frame and adjacent construction are installed correctly and are ready to receive work of this Section.

Verify that utilities are in correct location and are of correct capacities for specified products.

Proceed with installation only after unsatisfactory conditions have been corrected.

INSTALLATION

Specifier Note: Delete the optional text in the following paragraph if shop drawings are not required for a specific project.

Install air curtains where indicated on Drawings and accordance with [shop drawings and] manufacturer’s instructions.  Provide clearance to permit servicing and maintenance.

Securely install air curtains plumb, level, and as close as practical to top of opening and face of wall.

Install switches where indicated on Drawings.

CONNECTIONS

Specifier Note:  Retain the following paragraph if electric heated air curtains are retained in Part 2 - Products.

Connect air curtain to utilities as specified in Division 26 sections.

FIELD QUALITY CONTROL

Provide a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Test and operate air curtain to be sure that it performs as intended.

ADJUSTING

Adjust fan speed to prepare installed products to perform properly.

Specifier Note: Delete the optional text in the following paragraph if not required for a specific project.

Adjust discharge nozzles to deflect air outward [unless otherwise required].

CLEANING

Clean air curtain prior to commissioning.

Repair or repaint damage to finishes on exposed-to-view surfaces.

SYSTEM STARTUP

Specifier Note:  Retain optional text in paragraph below if required for a specific project.

Test and operate air curtains to ensure that they perform as intended.  Adjust discharge nozzles to deflect air outward [unless otherwise required].

DEMONSTRATION

Demonstrate for Owner’s maintenance personnel how to adjust, operate, and maintain air curtains.

END OF SECTION

© 2011 Berner International Corporation.  All Rights Reserved.

A copyright license to reproduce this specification is hereby granted

to non-manufacturing engineers, architects and specification writers.

Revd 10/17